Office of the Fire Marshal (BFP)

Automatic Sprinkler Systems
Inspection, Testing, and Maintenance
of Dry Pipe Sprinkler Systems

| Property Name: |  |  |  |  |  |  | Inspector: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Property Address: |  |  |  |  |  |  | Contract No.: |  |  |  |
| Phone Number: |  |  |  |  |  |  | Date: |  |  |  |
| This Report Covers: |  |  | Monthly |  | Quarterly |  | Annual |  |  |  |
|  |  |  | Three-Year |  | Five-Year |  |  |  |  |  |

Inspections

Monthly

|  | Yes |  | No |  | N/A | Gauges—normal air and water pressure maintained |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Control Valves |
|  | Yes |  | No |  | N/A | In the correct (open or closed) position |
|  | Yes |  | No |  | N/A | Sealed, locked, or supervised |
|  | Yes |  | No |  | N/A | Accessible |
|  | Yes |  | No |  | N/A | Free from damage or leaks |
|  | Yes |  | No |  | N/A | Proper signage |
|  |  |  |  |  |  | Dry Pipe Valves |
|  | Yes |  | No |  | N/A | Exterior is free of damage, trim valves are in correct open or closed position, and intermediate chamber is not leaking |

Quarterly

|  | Yes |  | No |  | N/A | Alarm devices—free of damage |
| --- | --- | --- | --- | --- | --- | --- |
|  | Yes |  | No |  | N/A | Hydraulic data nameplate—securely attached to riser/legible |
|  |  |  |  |  |  | Fire Department Connections |
|  | Yes |  | No |  | N/A | Visible and accessible |
|  | Yes |  | No |  | N/A | Coupling/swivels operate correctly |
|  | Yes |  | No |  | N/A | Plugs/caps are in place |
|  | Yes |  | No |  | N/A | Gaskets are not damaged |
|  | Yes |  | No |  | N/A | Identification signs are in place |
|  | Yes |  | No |  | N/A | Ball drip is functional |
|  | Yes |  | No |  | N/A | FDC clapper is functional |
|  |  |  |  |  |  | Pressure Reducing Valve |
|  | Yes |  | No |  | N/A | In the open position/not leaking |
|  | Yes |  | No |  | N/A | Maintaining downstream pressure |
|  | Yes |  | No |  | N/A | In good condition |

Annual			        Sprinklers

|  | Yes |  | No |  | N/A | No damage or leaks |
| --- | --- | --- | --- | --- | --- | --- |
|  | Yes |  | No |  | N/A | Free of corrosion, foreign material, or paint |
|  | Yes |  | No |  | N/A | Installed in proper orientation |
|  | Yes |  | No |  | N/A | Fluid in glass bulbs |
|  | Yes |  | No |  | N/A | Spare sprinklers—proper number and type. Complete with wrench? |
|  | Yes |  | No |  | N/A | Hangers and seismic bracing—not damaged or loose |
|  |  |  |  |  |  | Pipes and Fittings |
|  | Yes |  | No |  | N/A | In good condition/no external corrosion |
|  | Yes |  | No |  | N/A | No leaks or mechanical damage |
|  | Yes |  | No |  | N/A | Correct alignment—no external loads |
|  | Yes |  | No |  | N/A | Dry pipe valve interior—following trip test |
|  | Yes |  | No |  | N/A | Building—prior to onset of freezing weather—all openings are closed, no water-filled pipe is exposed to freezing temps |

Five-Year

|  | Yes |  | No |  | N/A | Obstruction inspection—no foreign or obstructing material found |
| --- | --- | --- | --- | --- | --- | --- |
|  | Yes |  | No |  | N/A | Check valve—internal moves freely, in good condition |
|  | Yes |  | No |  | N/A | Dry pipe valve strainers, filters, and orifices internal inspection |

Test

Quarterly

|  | Yes |  | No |  | N/A | Alarm devices—water motor gong |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Yes |  | No |  | N/A | Main drain test—if the sole supply is through a backflow preventer or pressure reducing valve |  |  |  |  |
|  |  |  |  |  |  | Static psi |  | Residual psi |  |  |
|  | Yes |  | No |  | N/A | Do results differ by more than 10% from previous test? |  |  |  |  |
|  | Yes |  | No |  | N/A | Priming water—test level |  |  |  |  |
|  | Yes |  | No |  | N/A | Low air alarm—test per manufacturer’s instructions |  |  |  |  |
|  | Yes |  | No |  | N/A | Quick opening device tested |  |  |  |  |

Semi-annual

|  | Yes |  | No |  | N/A | Supervisory switch functions |
| --- | --- | --- | --- | --- | --- | --- |
|  | Yes |  | No |  | N/A | Alarm devices—inspectors test or bypass opened/obstructed waterflow |

Annual

|  | Yes |  | No |  | N/A | Main drain test | Static psi: |  |  | Residual psi: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Yes |  | No |  | N/A | Do results differ by more than 10% from previous test? |  |  |  |  |  |  |  |
|  | Yes |  | No |  | N/A | All control valves operated through full range of motion and returned to normal position. |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Dry pipe valve trip test (partial flow) |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Water pressure |  |  | Air pressure |  |  |  |  |
|  |  |  |  |  |  | Tripping air pressure |  |  | Trip time |  |  |  | (sec) |
|  | Yes |  | No |  | N/A | Results comparable to previous tests |  |  |  |  |  |  |  |
|  | Yes |  | No |  | N/A | Backflow preventer—backflow test |  |  |  |  |  |  |  |
|  | Yes |  | No |  | N/A | Backflow preventer—flow test |  |  |  |  |  |  |  |

Three-Year

|  | Yes |  | No |  | N/A | Dry pipe valve—full flow trip test |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Water pressure |  |  | Air pressure |  |  |  |  |
|  |  |  |  |  |  | Tripping air pressure |  |  | Trip time |  |  |  | (sec) |
|  |  |  |  |  |  | Water delivery time |  | (min.) |  |  | (sec) |  |  |
|  | Yes |  | No |  | N/A | Results comparable to previous years |  |  |  |  |  |  |  |

Five-Year

|  | Yes |  | No |  | N/A | Gauges tested or replaced |
| --- | --- | --- | --- | --- | --- | --- |
|  | Yes |  | No |  | N/A | Pressure reducing valve—flow test and comparable to previous results |

Routine Maintenance

|  | Yes |  | No |  | N/A | Sprinklers tested or replaced per appropriate testing schedule |
| --- | --- | --- | --- | --- | --- | --- |

Comments:

| Signature: |  |  | Date: |  |
| --- | --- | --- | --- | --- |
| License/Certification No.: |  |  |  |  |